## V-II OU DIP-SW settings
V-II outdoor unit Dip-Switch settings
Outdoor unit Capacity setting
DIP Switch |  | Switch No. | ON | OFF | Model
SW 101 | Set 1 - | 1 | x |  | AJY144LALH | Setting required for all outdoor units
|  | 2 |  | x
|  | 3 |  | x
|  | 4 |  | x
|  | 1 |  | x | AJY126LALH
|  | 2 | x
|  | 3 | x
|  | 4 |  | x
|  | 1 |  | x | AJY108LALH
|  | 2 | x
|  | 3 |  | x
|  | 4 |  | x
|  | 1 |  | x | AJYA90LALH
|  | 2 |  | x
|  | 3 | x
|  | 4 |  | x
|  | 1 |  | x | AJYA72LALH
|  | 2 |  | x
|  | 3 |  | x
|  | 4 |  | x
Not used and must be fixed at OFF!!
DIP Switch |  | Switch No. | ON | OFF | Model
SW 102 | Set 2 - | 1 |  | x | all V-II outdoor units | Setting required for all outdoor units
|  | 2 |  | x
|  | 3 |  | x
|  | 4 |  | x
Outdoor unit type setting (master/slave) Set 3-1 and Set 3-2 | [5 empty] | RS485 Bus communication settings
Outdoor unit combination setting (M/MS/MSS) Set 3-3 and Set 3-4
DIP Switch |  | Switch No. | ON | OFF | setting
SW103 | Set 3 - | 1 |  | x | Master | Setting required for all outdoor units
|  | 2 |  | x
|  | 1 |  | x | Slave 1
|  | 2 | x
|  | 1 | x |  | Slave 2
|  | 2 |  | x
|  | 3 |  | x | Master only | Setting required only for Master outdoor unit
|  | 4 |  | x
|  | 3 |  | x | Master + Slave 1
|  | 4 | x
|  | 3 | x |  | Master + Slave 1 + 2
|  | 4 |  | x
Not used and must be fixed at OFF!!
DIP Switch |  | Switch No. | ON | OFF | Model
SW 104 | Set 4 - | 1 |  | x | all V-II outdoor units | Setting required for all outdoor units
|  | 2 |  | x
|  | 3 |  | x
|  | 4 |  | x
Outdoor unit combination setting (M/MS/MSS) Set 5-1 and Set 5-2 | [5 empty] | Lon Bus communication settings
Terminal resistor setting Set 5-4 (Set 5-3 is must be fixed at OFF !! ) | [5 empty] | Terminal Resistor
DIP Switch |  | Switch No. | ON | OFF | setting
SW110 | Set 5 - | 1 |  | x | Master only | setting required for all outdoor units
|  | 2 |  | x
|  | 1 |  | x | Master + Slave 1
|  | 2 | x
|  | 1 | x |  | Master + Slave 1 + 2
|  | 2 |  | x
|  | 3 |  | x | fixed at OFF
|  | 4 |  | x | inactive | setting required only for Master outdoor unit
|  | 4 | x |  | active

## Outdoor Function Settings
F1 : Monitor mode V-II Outdoor Unit
Function No. | Item |  |  | Unit
0 | Connected Indoor unit number |  |  | 1 till 48
1 | Software version Main PCB
2 | Software version Inverter PCB
3 | Software version Transmission PCB
10 | Fan rotation speed |  |  | rpm
11 | Inverter Compressor rotation Speed |  |  | rps
12 | Current of Inverter Compressor |  |  | A
13 | Current of Constant Speed Compressor |  |  | A
14 | EEV1 Pulse (heating mode) |  |  | Pls
15 | EEV2 Pulse (subcooler) |  |  | Pls
20 | Time count for power connection |  |  | x10 hours
21 | Time count for Inverter Compressor operation time (cooling mode) |  |  | x10 hours
22 | Time count for Inverter Compressor operation time (heating mode) |  |  | x10 hours
23 | Time count for Constant Speed Compressor operation |  |  | x10 hours
30 | Temperatur Thermistor 1 (discharge temperatur Inverter Compressor) |  |  | °C or °F
31 | Temperatur Thermistor 2 (discharge temperature fixed speed Compressor) |  |  | °C or °F
32 | Temperatur Thermistor 3 (outdoor temperature) |  |  | °C or °F
33 | Temperatur Thermistor 4 (suction pipe temperature) |  |  | °C or °F
34 | Temperatur Thermistor 5 (Heat exchanger outlet cooling mode / inlet heating mode) |  |  | °C or °F
35 | Temperatur Thermistor 6 (liquid inlet subcooler for cooling mode / outlet heating mode) |  |  | °C or °F
36 | Temperatur Thermistor 7 (liquid outlet subcooler for cooling mode / inlet heating mode) |  |  | °C or °F
37 | Temperatur Thermistor 8 (inlet evaporating temperature subcooler) |  |  | °C or °F
38 | Temperatur Thermistor 9 (suction temperature behind subcooler) |  |  | °C or °F
39 | Temperatur Thermistor 10 (Inverter Compressor temperature) |  |  | °C or °F
40 | Temperatur Thermistor 11 (Fixed Speed Compressor temperature) |  |  | °C or °F
50 | Pressure Sensor 1 ( high pressure ) |  |  | Mpa
51 | Pressure Sensor 2 ( low pessure ) |  |  | Mpa
F2 : Function Setting V-II Outdoor Unit
Function No | Item | No | Setting | Set for Master | Set for Slave
0 | Pipe Length | 00 | 40 - 65m | 〇
|  | 01 | 7.5 - 40m
|  | 02 | 65 - 90m
|  | 03 | 90 - 120m
|  | 04 | 120 - 150m
10 | Sequential Start | 00 | 0 Sec | 〇
|  | 01 | 21 Sec
|  | 02 | 42 Sec
|  | 03 | 63 Sec
11 | Capacity Shift for Cooling | 00 | Standard | 〇
|  | 01 | energy save mode ( +2°C)
|  | 02 | High Capacity 1 (-2°C)
|  | 03 | High Capacity 2 (-4°C)
|  | 04 | High Capacity 3 (-5°C)
12 | Capacity Shift for Heating | 00 | Standard | 〇
|  | 01 | energy save mode ( -2°C)
|  | 02 | High Capacity 1 (+2°C)
|  | 03 | High Capacity 2 (+4°C)
13 | Forbidden(Defrost set temp at Finish) | 00 | Standard | 〇 | 〇
|  | 01 | Higher Temp
20 | Select of external input ON/OFF function | 00 | All OFF | 〇
|  | 01 | Emergency stop
21 | Priority setting of operation mode | 00 | First command priority | 〇
|  | 01 | Outdoor unit external input priority
|  | 02 | Master indoor unit priority
22 | Snow falling prevention | 00 | Standard | 〇
|  | 01 | Validity
23 | Snow falling prevention interval | 00 | Standard (30min) | 〇
|  | 01 | Short 1 (5min)
|  | 02 | Short 2 (10min)
|  | 03 | Short 3 (20min)
24 | High static pressure mode | 00 | Standard | 〇 | 〇
|  | 01 | High pressure1( - 30Pa)
|  | 02 | High pressure2 (30-80Pa)
27 | Forbidden (Error nitification) | 00 | Notification | 〇
|  | 01 | No notification
28 | Forbidden (Temperature unit display C or F) | 00 | C | 〇 | 〇
|  | 01 | F
29 | Forbidden (Pressure unit display Mpa or psi) | 00 | MPa | 〇 | 〇
|  | 01 | psi
30 | Peak cut control | 00 | 0% | 〇
|  | 01 | 40%
|  | 02 | 60%
|  | 03 | 80%
40 | Quiet operation priority | 00 | Capacity priority | 〇
|  | 01 | Low noise priority
41 | Quiet operation mode mode | 00 | Off | 〇
|  | 01 | Quiet operation mode
42 | Quiet operatio level | 00 | Level 1 (55dB) | 〇 | 〇
|  | 01 | Level 2 (50dB)
70 | Forbidden
F3 : Mode Setting
Function No | Item
0 | Test run cooling
1 | Test run heating
2 | Test run finish
3 | Forbidden (Forced oil recovery)
4 | Forbidden (Forced defrost)
10 | Auto adress for signal amplifier)
11 | Auto adress for indoor units
20 | Forbidden
21 | Vacuum mode (open all EEV´s of indoor and outdoor unit)
30 | Clear the error history
31 | Clear the operation record just before error
32 | Clear the time count of power supply
33 | Clear the Inverter Compressor operation count
34 | Clear the constant Compressor operation count
35 | Clear the all field seting to initial
40 | Reset the error
91 | Central control forced release (all limitation set by Cental Control will be released)
F9 : Error History Mode
0 | 1 time ago (newest error) |  |  | Please refer to Error Code list Outdoor unit
1 | 2 times ago
2 | 3 times ago
3 | 4 times ago
4 | 5 times ago
5 | 6 times ago
6 | 7 times ago
7 | 8 times ago
8 | 9 times ago
9 | 10 times ago (oldest error)

## Indoor Function Settings
Function | Function Number | Setting Number
Indoor unit address | 1 | 00-63 | 00-63
Refrigerant circuit address | 2 | 00-99 | 00-99
Interval time of filter clean sign | 11 | 00 | Standard | ●
|  | 01 | Longer
|  | 02 | Shorter
Indicator selection of filter clean sign | 13 | 00 | Enable | ●
|  | 01 | Disable
|  | 02 | Display only central control
High Ceiling mode | 20 | 00 | Standard | ●
|  | 01 | Ceiling 1
|  | 02 | Ceiling 2
Draft Prevention | 23 | 00 | Standard | ●
|  | 01 | upward(Draft prevention)
Horizontal swing air flow direction | 24 | 00 | Standard | ●
|  | 01 | Left half
|  | 02 | Right half
Room Temp correct coefficient for cooling | 30 | 00 | 0℃ | ●
|  | 01 | +2℃
|  | 02 | -2℃
Room Temp correct coefficient for heating | 31 | 00 | 0℃ | ●
|  | 01 | +8℃
|  | 02 | +4℃
|  | 03 | -2℃
Auto Restart | 40 | 00 | Enable | ●
|  | 01 | Disable
Cool air prevention | 43 | 00 | Enable | ●
|  | 01 | Disable (ventilation mode)
External control function | 46 | 00 | Start/stop | ●
|  | 01 | Emergency stop
Error display | 47 | 00 | All | ●
|  | 01 | Central Control only

## All combinations
Dip Switch table for all possible V-II Outdoor unit combinations
Space saving combinations
AJYA72LALH
Master Outdoor unit (AJYA72LALH) |  | Set 1 |  |  |  | Set 2 |  |  |  | Set 3 |  |  |  | Set 4 |  |  |  | Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW110 4
OFF | bar: SW 101 1 to SW110 3
AJYA90LALH
Master Outdoor unit (AJYA90LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 3; SW110 4
OFF | bar: SW 101 1 to SW 101 2; SW 101 4 to SW110 3
AJY108LALH
Master Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW110 4
OFF | bar: SW 101 1; SW 101 3 to SW110 3
AJY126LALH
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW110 4
OFF | bar: SW 101 1; SW 101 4 to SW110 3
AJY144LALH
Master Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW110 4
OFF | bar: SW 101 2 to SW110 3
AJY162LALH (AJYA90LALH + AJYA72LALH)
Master Outdoor unit (AJYA90LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 3; SW103 4; SW110 2; SW110 4
OFF | bar: SW 101 1 to SW 101 2; SW 101 4 to SW103 3; SW104 1 to SW110 1; SW110 3
Slave 1 Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 2; SW110 2
OFF | bar: SW 101 1 to SW103 1; SW103 3 to SW110 1; SW110 3 to SW110 4
AJY180LALH (AJY108LALH + AJYA72LALH)
Master Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 4; SW110 2; SW110 4
OFF | bar: SW 101 1; SW 101 3 to SW103 3; SW104 1 to SW110 1; SW110 3
Slave 1 Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 2; SW110 2
OFF | bar: SW 101 1 to SW103 1; SW103 3 to SW110 1; SW110 3 to SW110 4
AJY198LALH (AJY108LALH + AJYA90LALH)
Master Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 4; SW110 2; SW110 4
OFF | bar: SW 101 1; SW 101 3 to SW103 3; SW104 1 to SW110 1; SW110 3
Slave 1 Outdoor unit (AJYA90LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 3; SW103 2; SW110 2
OFF | bar: SW 101 1 to SW 101 2; SW 101 4 to SW103 1; SW103 3 to SW110 1; SW110 3 to SW110 4
AJY216LALH (AJY108LALH + AJY108LALH)
Master Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 4; SW110 2; SW110 4
OFF | bar: SW 101 1; SW 101 3 to SW103 3; SW104 1 to SW110 1; SW110 3
Slave 1 Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 2; SW110 2
OFF | bar: SW 101 1; SW 101 3 to SW103 1; SW103 3 to SW110 1; SW110 3 to SW110 4
AJY234LALH (AJY126LALH + AJY108LALH)
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 4; SW110 2; SW110 4
OFF | bar: SW 101 1; SW 101 4 to SW103 3; SW104 1 to SW110 1; SW110 3
Slave 1 Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 2; SW110 2
OFF | bar: SW 101 1; SW 101 3 to SW103 1; SW103 3 to SW110 1; SW110 3 to SW110 4
AJY252LALH (AJY144LALH + AJY108LALH)
Master Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 4; SW110 2; SW110 4
OFF | bar: SW 101 2 to SW103 3; SW104 1 to SW110 1; SW110 3
Slave 1 Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 2; SW110 2
OFF | bar: SW 101 1; SW 101 3 to SW103 1; SW103 3 to SW110 1; SW110 3 to SW110 4
AJY270LALH (AJY144LALH + AJY126LALH)
Master Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 4; SW110 2; SW110 4
OFF | bar: SW 101 2 to SW103 3; SW104 1 to SW110 1; SW110 3
Slave 1 Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 2; SW110 2
OFF | bar: SW 101 1; SW 101 4 to SW103 1; SW103 3 to SW110 1; SW110 3 to SW110 4
AJY288LALH (AJY144LALH + AJY144LALH)
Master Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 4; SW110 2; SW110 4
OFF | bar: SW 101 2 to SW103 3; SW104 1 to SW110 1; SW110 3
Slave 1 Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 2; SW110 2
OFF | bar: SW 101 2 to SW103 1; SW103 3 to SW110 1; SW110 3 to SW110 4
AJY306LALH (AJY108LALH + AJY108LALH + AJYA90LALH)
Master Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 1; SW 101 3 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Slave 1 Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 2; SW110 1
OFF | bar: SW 101 1; SW 101 3 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Slave 2 Outdoor unit (AJYA90LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 3; SW103 1; SW110 1
OFF | bar: SW 101 1 to SW 101 2; SW 101 4 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY324LALH (AJY108LALH + AJY108LALH + AJY108LALH)
Master Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 1; SW 101 3 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Slave 1 Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 2; SW110 1
OFF | bar: SW 101 1; SW 101 3 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Slave 2 Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 1; SW110 1
OFF | bar: SW 101 1; SW 101 3 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY342LALH (AJY126LALH + AJY108LALH + AJY108LALH)
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 1; SW 101 4 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Slave 1 Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 2; SW110 1
OFF | bar: SW 101 1; SW 101 3 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Slave 2 Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 1; SW110 1
OFF | bar: SW 101 1; SW 101 3 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY360LALH (AJY144LALH + AJY108LALH + AJY108LALH)
Master Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 2 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Slave 1 Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 2; SW110 1
OFF | bar: SW 101 1; SW 101 3 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Slave 2 Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 1; SW110 1
OFF | bar: SW 101 1; SW 101 3 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY378LALH (AJY144LALH + AJY126LALH + AJY108LALH)
Master Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 2 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Slave 1 Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 2; SW110 1
OFF | bar: SW 101 1; SW 101 4 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Slave 2 Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 1; SW110 1
OFF | bar: SW 101 1; SW 101 3 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY396LALH (AJY144LALH + AJY144LALH + AJY108LALH)
Master Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 2 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Slave 1 Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 2; SW110 1
OFF | bar: SW 101 2 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Slave 2 Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 1; SW110 1
OFF | bar: SW 101 1; SW 101 3 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY414LALH (AJY144LALH + AJY144LALH + AJY126LALH)
Master Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 2 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Slave 1 Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 2; SW110 1
OFF | bar: SW 101 2 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Slave 2 Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 1; SW110 1
OFF | bar: SW 101 1; SW 101 4 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY432LALH (AJY144LALH + AJY144LALH + AJY144LALH)
Master Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 2 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Slave 1 Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 2; SW110 1
OFF | bar: SW 101 2 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Slave 2 Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 1; SW110 1
OFF | bar: SW 101 2 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
Energy Efficiency Combination
AJY144LALHH (AJYA72LALH + AJYA72LALH)
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 4; SW110 2; SW110 4
OFF | bar: SW 101 1 to SW103 3; SW104 1 to SW110 1; SW110 3
Slave 1 Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 2; SW110 2
OFF | bar: SW 101 1 to SW103 1; SW103 3 to SW110 1; SW110 3 to SW110 4
AJY198LALHH (AJY126LALH + AJYA72LALH)
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 4; SW110 2; SW110 4
OFF | bar: SW 101 1; SW 101 4 to SW103 3; SW104 1 to SW110 1; SW110 3
Slave 1 Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 2; SW110 2
OFF | bar: SW 101 1 to SW103 1; SW103 3 to SW110 1; SW110 3 to SW110 4
AJY216LALHH (AJYA72LALH + AJYA72LALH + AJYA72LALH)
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 1 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 2; SW110 1
OFF | bar: SW 101 1 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 1; SW110 1
OFF | bar: SW 101 1 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY232LALHH (AJYA90LALH + AJYA72LALH + AJYA72LALH)
Master Outdoor unit (AJYA90LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 3; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 1 to SW 101 2; SW 101 4 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 2; SW110 1
OFF | bar: SW 101 1 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 1; SW110 1
OFF | bar: SW 101 1 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY252LALHH (AJY108LALH + AJYA72LALH + AJYA72LALH)
Master Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 1; SW 101 3 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 2; SW110 1
OFF | bar: SW 101 1 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 1; SW110 1
OFF | bar: SW 101 1 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY270LALHH (AJY126LALH + AJYA72LALH + AJYA72LALH)
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 1; SW 101 4 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 2; SW110 1
OFF | bar: SW 101 1 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 1; SW110 1
OFF | bar: SW 101 1 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY288LALHH (AJY108LALH + AJY108LALH + AJYA72LALH)
Master Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 1; SW 101 3 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Master Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 2; SW110 1
OFF | bar: SW 101 1; SW 101 3 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 1; SW110 1
OFF | bar: SW 101 1 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY306LALHH (AJY126LALH + AJY108LALH + AJYA72LALH)
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 1; SW 101 4 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Master Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 2; SW110 1
OFF | bar: SW 101 1; SW 101 3 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 1; SW110 1
OFF | bar: SW 101 1 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY324LALHH (AJY126LALH + AJY126LALH + AJYA72LALH)
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 1; SW 101 4 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 2; SW110 1
OFF | bar: SW 101 1; SW 101 4 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Master Outdoor unit (AJYA72LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW103 1; SW110 1
OFF | bar: SW 101 1 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY360LALHH (AJY126LALH + AJY126LALH + AJY108LALH)
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 1; SW 101 4 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 2; SW110 1
OFF | bar: SW 101 1; SW 101 4 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Master Outdoor unit (AJY108LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2; SW103 1; SW110 1
OFF | bar: SW 101 1; SW 101 3 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY378LALHH (AJY126LALH + AJY126LALH + AJY126LALH)
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 1; SW 101 4 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 2; SW110 1
OFF | bar: SW 101 1; SW 101 4 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 1; SW110 1
OFF | bar: SW 101 1; SW 101 4 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4
AJY396LALHH (AJY144LALH + AJY126LALH + AJY126LALH)
Master Outdoor unit (AJY144LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 1; SW103 3; SW110 1; SW110 4
OFF | bar: SW 101 2 to SW103 2; SW103 4 to SW104 4; SW110 2 to SW110 3
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 2; SW110 1
OFF | bar: SW 101 1; SW 101 4 to SW103 1; SW103 3 to SW104 4; SW110 2 to SW110 4
Master Outdoor unit (AJY126LALH) |  | SW 101 1: Set 1; SW102 1: Set 2; SW103 1: Set 3; SW104 1: Set 4; SW110 1: Set 5
|  | SW 101 |  |  |  | SW102 |  |  |  | SW103 |  |  |  | SW104 |  |  |  | SW110
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
ON | bar: SW 101 2 to SW 101 3; SW103 1; SW110 1
OFF | bar: SW 101 1; SW 101 4 to SW102 4; SW103 2 to SW104 4; SW110 2 to SW110 4

## indoor unit Dip Switches
Indoor unit Dip Switch settings
SET 1 | SW1 | 1 | Indoor unit capacity setting for EEV control (please refer to capacity table)
2
3
4
SET 2 | SW2 | 1
|  | 2 | external input select (edge/pulse)
|  | 3 | fixed at OFF
|  | 4 | fixed at OFF
SET 3 | SW3 or SW601 | 1 | wireless RC custom code switches
2
|  | 3 | fixed at OFF
|  | 4 | fixed at OFF
SET 4 | SW4 or SW602 | 1 | fixed at OFF
|  | 2 | fixed at OFF
|  | 3 | fixed at OFF
|  | 4 | fixed at OFF
SET 5 | SW5 | 1 | fixed at OFF
|  | 2 | fixed at OFF
|  | 3 | fixed at OFF
|  | 4 | fixed at OFF
IU AD x 10 | SW6 | Rotary Switch 0-10 | indoor unit address setting value
IU AD x 1 | SW7 | Rotary Switch 0-10
REF AD x 10 | SW8 | Rotary Switch 0-10 | refrigerant circuit address setting value
REF AD x 1 | SW9 | Rotary Switch 0-10
RC AD | SW10 | Rotary Switch 0-10 | remote controller address setting

## OU Fan Speed
Steps | AJYA72-108LALH | AJY126-144LALH | Control DC Voltage | Feed Back Voltage
16 | 880 rpm | 920 rpm | 4,1 V DC | 7,8 V DC
15 | 860 rpm | 870 rpm | 4,0 V DC | 7,8 V DC
14 | 820 rpm | 820 rpm | 3,8 V DC | 7,8 V DC
13 | 720 rpm | 720 rpm | 3,5 V DC | 7,8 V DC
12 | 600 rpm | 600 rpm | 3,2 V DC | 7,8 V DC
11 | 500 rpm | 500 rpm | 3,0 V DC | 7,8 V DC
10 | 420 rpm | 420 rpm | 2,8 V DC | 7,8 V DC
9 | 360 rpm | 360 rpm | 2,7 V DC | 7,8 V DC
8 | 320 rpm | 320 rpm | 2,65 V DC | 7,8 V DC
7 | 300 rpm | 300 rpm | 2,6 V DC | 7,8 V DC
6 | intermittent 6 | intermittent 6 | 2,6 V DC ON/OFF | 7,8 V DC ON/OFF
5 | intermittent 5 | intermittent 5 | 2,6 V DC ON/OFF | 7,8 V DC ON/OFF
4 | intermittent 4 | intermittent 4 | 2,6 V DC ON/OFF | 7,8 V DC ON/OFF
3 | intermittent 3 | intermittent 3 | 2,6 V DC ON/OFF | 7,8 V DC ON/OFF
2 | intermittent 2 | intermittent 2 | 2,6 V DC ON/OFF | 7,8 V DC ON/OFF
1 | intermittent 1 | intermittent 1 | 2,6 V DC ON/OFF | 7,8 V DC ON/OFF
0 | Off | Off | OFF | OFF

## Error List OU
Outdoor Unit Error Code List
Error Code | Error Contents | Error Code | Error Contents
(----) | Initial setting Error | 83.1 | Liquid Pipe Temp. Sensor 1 inlet Error
13.1 | Communication Error between Outdoor units | 83.2 | Liquid Pipe Temp. Sensor 2 outlet Error
14.1 | Outdoor Unit Network communication 1 Error | 84.1 | Current Sensor 1 Error
14.2 | Outdoor Unit Network communication 2 Error | 86.1 | Discharge Pressure Sensor Error
14.5 | number of indoor unit shortage
28.1 | Auto Address Setting Error | 86.3 | Suction Pressure Sensor Error
28.4 | Signal Amplifier Address Error | 86.4 | High Pressure Switch 1 Error
5U.1 | Indoor unit Error | 86.5 | High Pressure Switch 2 Error
61.5 | Outdoor unit Reverse Phase, missing Phase Error | 92.1 | Compressor 2 Error
62.3 | Outdoor Unit EEPROM Access Error | 92.2 | Compressor 2 Current Value Error
62.6 | Inverter Communication Error | 93.1 | Inverter Compressor Start up Error
62.8 | Outdoor Unit EEPROM Data Error | 94.1 | Trip Detection
63.1 | Inverter Error | 95.5 | Compressor Motor Loss of Synchronization
67.2 | Inverter PCB Momentary Power Failure Detection | 97.1 | Outdoor Unit Fan Motor Lock Error
68.1 | Magnetic Relay Error | 97.4 | Outdoor Unit Fan Motor Undervoltage
68.2 | Rush Current Limiting Resistor Temp. Rise Protection | 97.5 | Outdoor Unit Fan Motor Temperature Abnormal
69.1 | Outdoor unit Communcation PCB Parrallel Communication Error | 9U.2 | Slave Unit Error
71.1 | Discharge Temperature Sensor 1 Error | A1.1 | Discharge Temperature 1 Abnormal
71.2 | Discharge Temperature Sensor 2 Error | A2.1 | Discharge Temperature 2 Abnormal
72.2 | Compressor Temperature sensor 1 Error | A3.1 | Compressor 1 Temperature Abnormal
72.3 | Compressor Temperature sensor 2 Error | A3.2 | Compressor 2 Temperature Abnormal
73.3 | Outdoor Unit Heat Ex. Liquid Temp. Sensor Error | A4.1 | High Pressure Abnormal
74.1 | Outdoor Temperature Sensor Error | A4.2 | High Pressure Protection 1
75.1 | Suction Gas Temp. Sensor Error | A4.3 | High Pressure Protection 2
77.1 | Heat Sink Temperature Sensor Error | A5.1 | Low Pressure Abnormal
82.1 | Sub-cool Heat Ex. Gas Inlet Temp. Sensor Error | AC.4 | Heat Sink Temperature Abnormal
82.2 | Sub-cool Heat Ex. Gas Outlet Temp. Sensor Error